## punchlist
status | description | comments | date_orig | due_date | author_id | closure_id | supplier_id | system_id | floor_id | phase_id | cat_id | building_id | closed_by
0 | Diptube and sprayballs missing | To be provided by BLF before MC. Electropolishing to be done after dynamic tests, to avoid scratches. Fabiana Cortellini 28-MAR-2018: sprayballs and diptube checked during SAT. Refer to SAT protocol P16-0052-SAT MECHANICAL PROTOCOL R201. | ﻿2019-04-07 | ﻿2019-04-07 | SMON | SMON | BLF | R201 - Buffer Preparation Tank 12000L | LEVEL 1 | SAT | C | Building 341
0 | Nameplate missing | BLF to install it on site. Temporary label must be installed prior shipment. / Nameplate in place. Indication according to the construction drawing. | ﻿2019-04-07 | ﻿2019-04-07 | FCOR | FCOR | BLF | R201 - Buffer Preparation Tank 12000L | LEVEL 1 | SAT | B | Building 341
0 | Agitator and load cells not installed, no check done | Agitator and load cells to be installed on site Fabiana Cortellini 19-APR-2018: agitator has been installed and checked. Load cells not yet installed. Refer to prolog item 27. | ﻿2019-04-07 | ﻿2019-04-07 | FCOR | FCOR | BLF | R201 - Buffer Preparation Tank 12000L | LEVEL 1 | SAT | A | Building 341
0 | Some ingold plugs are damaged | To be checked by BLF and replaced Fabiana Cortellini 07-JUN-2018: ingold plugs have been checked during SAT. | ﻿2019-04-07 | ﻿2019-04-07 | DPAT | DPAT | BLF | R201 - Buffer Preparation Tank 12000L | LEVEL 1 | SAT | C | Building 341
0 | Earthing lugs not found | BLF to do it on the bracket to do in the same time the link from above to below the load cell and the grounding. Fabiana Cortellini 04-APR-2018: Earthing lugs have been installed. | ﻿2019-04-07 | ﻿2019-04-07 | DPAT | DPAT | BLF | R201 - Buffer Preparation Tank 12000L | LEVEL 1 | SAT | B | Building 341
0 | N14 (Manway): damage/scratch on manway gasket, without impact on the pressure tests performed | BLF to exchange the gasket. Fabiana Cortellini 30-MAY-2018: refer to item 8819. | ﻿2019-04-07 | ﻿2019-04-07 | DPAT | DPAT | BLF | R201 - Buffer Preparation Tank 12000L | LEVEL 1 | SAT | A | Building 341
0 | Nuts of hadhole/sightglass damaged (just visual defect, no effect on functionality and no safety issue). | Nuts to be exchanged on site Fabiana Cortellini 25-JUL-2018: nuts have been exchanged and checked. | ﻿2019-04-07 | ﻿2019-04-07 | DPAT | DPAT | BLF | R201 - Buffer Preparation Tank 12000L | LEVEL 1 | SAT | C | Building 341
0 | Studs (goujon) too shorts on some nozzles | BLF to check and exchange them on site Fabiana Cortellini 24-MAY-2018: studs have been exchanged by BLF on site. | ﻿2019-04-07 | ﻿2019-04-07 | DPAT | DPAT | BLF | R201 - Buffer Preparation Tank 12000L | LEVEL 1 | SAT | B | Building 341
0 | Vessel drawing is not in 'As built' revision | As built' revision to be included in the DOE by BLF Fabiana Cortellini 03-APR-2018: Construction drawing has been issued by BLF in rev 2.2, checked and approved with "no comment". | ﻿2019-04-07 | ﻿2019-04-07 | MQUA | MQUA | BLF | R201 - Buffer Preparation Tank 12000L | LEVEL 1 | SAT | A | Building 341
0 | Manufacturer's name plate is not available in the DOE | Manufacturer's name plate to be included in the DOE by BLF / document available in the orange binder | ﻿2019-04-07 | ﻿2019-04-07 | RCAR | RCAR | BLF | R201 - Buffer Preparation Tank 12000L | LEVEL 1 | SAT | A | Building 341

## validation (hidden)
HVAC | JEG | jsmith
DCS | NOV | janderson
EMS | JAC | sbre
CS | NOX | bmarie
WFI | ZET | FCOR
PW | AXI | DRYA
ELE | BLF | MGRA
ACP | BLF1 | SMON
EMS | PG | CCIA
BMS | BWT | RMAR
R201 - Buffer Preparation Tank 12000L | GEA | DPAT
R221 - Buffer Preparation Tank 12000L | CLY | MQUA
F483 - Centrifuge | SPI | MMEN
B292 - CIP Skid & Distribution System (Buffer Preparation) | TPI | JVID
B591 - CIP Skid & Distribution System (DSP) | BLF6 | RCAR
B216 - Buffer Storage Tank | MER | MCEC
ELEC-Normal - Electrical (Normal: Distribution) | NOI | BCRU
R482 - CIP Skid Centrifuge | MOA | FBUR
B217 - Buffer Storage Tank | CLE | DBOI
B192 - CIP Skid & Distribution System (Media) | SNE | ARIV
B293 - CIP Skid & Distribution System (Buffer Storage) | EIF | SIDO
B215 - Buffer Storage Tank | SIE | RTOR
C446 - Bioreactor 15000L | REV | EDES
C447 - Bioreactor 15000L | SEN | MPOZ
R118 - Media Preparation Tank 2500L | ISS | MCHR
R152 - Media Preparation Tank 10000L | MED | FCOR
R481 - Harvest Pool Tank 18000L | EME | MLUI
EPI3-D(Fr) - Eau Pour Injection (Froid) | VIS | RODO
EPI3-G&S - EPI Generation & Storage | TRA | VSCH
B155 - Buffer Storage Tank |  | AZAI
B204 - Buffer Storage Tank |  | MBEC
B205 - Buffer Storage Tank |  | LBEN
B206 - Buffer Storage Tank |  | GCOL
B225- Buffer Storage Tank |  | SWEG
B226 - Buffer Storage Tank |  | MHAE
R263 - NaOH 0.5M Preparation Tank 2000L |  | AKEL
B493 - CIP Skid & Distribution System (USP) |  | FTOF
R205 - Buffer Preparation Tank 2000L |  | SCAL
R206 - Buffer Preparation Tank 12000L |  | EURO
R211 - Buffer Preparation Tank 12000L |  | DGOE
F635 - Nanofiltration |  | MROL
R645 - Ultrafiltration |  | GTAG
AR - Instrument Air Distribution System |  | CBOS
C433 - Seed Bioreactor 2500L |  | AHER
R480 - Intermediate Pool Tank 5000L |  | MLAS
VT62 - Makeup & Exhaust Units - Zones 3, D, C |  | VGIM
VT63 - Recirculation Unit - Zone 3 - System 2 |  | CFAL
VT64 - Recirculation Unit - Zone 3 - System 3 |  | LRE
VT67 - Makeup & Exhaust Units - Zone N.C. - System 10
VT67 - Makeup & Exhaust Units - Zone N.C. - System 6
EV/EVC - Potable Water Distribution System
B214 - Buffer Storage Tank
VT66 - Recirculation Unit - Zone C - System 5
B224 - Buffer Storage Tank
F480 - Clarification Skid
C413 - Seed Bioreactor 90L
C423 - Seed Bioreactor 450L
ECC - Hot Water for Heating
ECB - Biowaste Collection & Storage System
RGS - Vent Systems
ECE - Ethanol Waste Collection System
ERF - Chilled Water Generation and Distribution System
R264 - NaOH 0.1M Preparation Tank 6300L
R612 - Filtrate Pool Tank 5000L
DeltaV 4 - Process Control System (DeltaV)
DeltaV 1 - Process Control System (DeltaV)
R641 - Formulation Pool Tank 250L
R631 - Eluate Pool Tank 3800L
R650 - Eluate Pool Tank 3800L (Inactivation)
L702 - NaOH 30% Distribution System
R621 - Eluate Pool Tank 3800L
Zone NC - System 6 - Zone NC - System 6
VT61 - Makeup & Exhaust Units 2 - Zone 2 - System 1
VT60 - Makeup & Exhaust Units 1 - Zone 2 - System 1
K630 - Chromatography Skid III - K630
K620 - Chromatography Skid II - K620
K610 - Chromatography Skid I - K610
EPI - EPI Generation (Existing)
EDP3-1 - Purified Water Generation & Storage System
VT65 - Recirculation Unit - Zone D - System 4
V080 - Steam Distribution V8
EDP3-2 - Purified Water Distribution System
VT66 - Recirculation Unit - Zone C - System 11
ELEC - Emergency - Electrical (Emergency System)
EPI3-D(Ch) - EPI Distribution (Chaud)
EI - Firewater Distribution System
V050 - Steam Distribution V5
ELEC-UPS - Electrical (UPS)
IP21 - Room Monitoring System (RMS: InfoPlus 21) and non HVAC related utilities
DCS WDOG - DCS Watchdog
DECT - DECT System
Zone 3 - System 3 - Zone 3 - System 3
Zone D - System 4 - Zone D - System 4
CSA - Finishes - CSA - Finishes
341 - Building Management System (BMS) - HVAC control for Building 341
Zone 2 - System 1 - Zone 2 - System 1
ELEC - 20kV - 20kV Electrical System
R152-H3 - Elevating Platform (R152-H3)
X647 - Bags-Filling Station
R301 - NaOH Dilution Skid
C444 - Bioreacteur De Production 13500L
C445 - Bioreacteur De Production 13500L
C443 - Bioreacteur De Production 13500L
R001V400 - HVAC System for Pumping Station
R004U2XX - HVAC System for Electrical Substation - MV Room (0.04)
R003V400 - HVAC System for Electrical Substation - TR2 Room
ECR - Process Waste Collection & Storage System
Zone NC - Other
Fire Det - Fire Detection
R001U2XX - HVAC System for Electrical Substation - TGBT Room
Hoist - Hoist: Agitator & Drums 200L (R152)
F473 - Centrifugeuse
CNR - Condensate Collection System
B191 - CIP Acid Mixing Skid
Hoist - Hoist: Centrifuge Bowl / Parts (F483)
RDP - RDP screen for DeltaV
LAN-Plant - Plant LAN for DeltaV: printer, Backup & Recovery and antivirus server
CSA - Hoist: Drums 200L (R205) [R205-H1]
CSA - Hoist: Clarification Filters (F480) [F480-H1]
CSA - Hoist: Waste 1 [WASTE-H1]
341-A03 - Elevator (341-A03)
Zone C - System 5 - Zone C - System 5
Zone 3 - System 2 - Zone 3 - System 2
ACP - Process Air Distribution System
GN2P - G/N2P Distribution System
L711 - N2 Liquid Storage System
N459 - Manifolds